# Introduction

Nuclear power occupies a singular position among low-carbon energy sources: it is the only technology that delivers firm, dispatchable, high-density electricity without direct greenhouse-gas emissions at a scale already proven across decades of operation. Yet the environments that make nuclear power possible, intense neutron and gamma fields, high temperatures, and chemically aggressive primary coolants (e.g., liquid sodium, molten fluoride salts, and high-pressure water), are precisely the environments that destroy the instruments needed to monitor and control it. Reliable radiation monitoring is not incidental to safe reactor operation; it is the primary mechanism by which operators verify that every defense-in-depth barrier to fission-product release, fuel cladding, reactor pressure boundary, and containment, remains intact. As the existing fleet ages and a generation of advanced and small modular reactors (SMRs) moves from concept to construction, the instrumentation technologies that have served the industry for half a century are confronting hard limits in both technical performance and economic viability. This dissertation investigates two complementary approaches to resolving that tension: the development of perovskite semiconductors as radiation-responsive detector materials, and the implementation of radiation-tolerant digital monitoring systems built on commercially available field-programmable gate arrays (FPGAs). Taken together, these efforts span the full stack from detector material to deployable system and aim to demonstrate that next-generation nuclear instrumentation can be both technically capable and represent a meaningful improvement in economic viability over current approaches.

## Nuclear Power and the Global Decarbonization Context

The scale of the decarbonization challenge facing the global electricity system makes any realistic pathway to net-zero heavily dependent on nuclear energy. At the COP28 climate summit in December 2023, twenty-two nations signed a declaration to triple global nuclear generating capacity from approximately 375 GWe to more than 1,125 GWe by 2050; that coalition has since grown to thirty-three countries . The International Energy Agency’s net-zero pathway requires nuclear capacity to reach approximately 1,079 GWe by 2050, demanding that annual investment in the sector roughly double from its current level of $65–75 billion to $120–150 billion per year by 2030 . The International Atomic Energy Agency (IAEA) has revised its projections upward for five consecutive years, with its 2025 high-case scenario projecting 992 GWe by 2050 .

The existing global fleet comprises approximately 408 operating reactors in thirty-one countries, with a combined net capacity that reached a record 369 GWe in 2024 . Nuclear electricity generation also set an all-time high of 2,667 TWh in 2024, narrowly surpassing the 2006 record, though nuclear’s share of global electricity has fallen to approximately 9% as variable renewables have expanded at a far faster pace . The fleet’s average age of 32.4 years, with 141 units exceeding 41 years of operation, makes life extension, instrumentation modernization, and new construction simultaneously urgent priorities.

Development of advanced reactors is more active and better funded than at any point in the last several decades. In the United States, TerraPower’s 345 MW(e) Natrium sodium-cooled fast reactor received its NRC construction permit in March 2026, the first commercial non-light-water reactor approval in over forty years . Kairos Power’s Hermes fluoride-salt-cooled test reactor began nuclear safety-related construction in 2025 , and X-energy’s Xe-100 pebble-bed high-temperature gas-cooled reactor is under development for an industrial host site with over $1.2 billion in DOE cost-share . Among light-water SMRs, GE-Hitachi’s BWRX-300 is under construction at Ontario’s Darlington site and has received a $400 million DOE award for deployment at TVA’s Clinch River site . Each of these programs introduces novel coolant chemistries, fuel geometries, and multi-module control architectures that existing monitoring technologies were never designed to address.

## The Regulatory Foundation for Radiation Monitoring

Continuous radiation monitoring across neutron flux, gamma dose, primary coolant activity, and effluent pathways is mandated by the regulatory foundations of nuclear operation, not merely encouraged by best practice. The NRC’s General Design Criteria (GDC), codified in 10 CFR 50 Appendix A, establish this requirement at the highest level of the licensing framework. GDC 13 requires instrumentation capable of monitoring all variables that affect the reactor core, coolant pressure boundary, and containment integrity; GDC 64 mandates monitoring of the containment atmosphere, recirculation spaces, and effluent pathways for radioactivity; and GDC 19 requires that control room operators maintain safe-shutdown capability with adequate instrumentation even under accident conditions . The IAEA mirrors these requirements through the Safety Requirements for Nuclear Power Plants (SSR-2/1) and provides detailed I&C system guidance in SSG-39 .

The technical scope of these monitoring requirements is exceptionally broad. Neutron flux measurement alone spans approximately twelve decades, from a few counts per second during refueling to approximately 1015 n cm​−2 s​−1 at full power, requiring three overlapping detector subsystems. Source-range monitors based on proportional counters or fission chambers operate in pulse-counting mode across the lowest six to seven decades during startup and shutdown. Intermediate-range monitors employ compensated ionization chambers in Campbell mode across approximately eight to ten decades. Power-range monitors using uncompensated boron-lined ionization chambers cover the upper two decades and are calibrated against secondary-side heat balance. Each of these subsystems must meet independent safety-channel redundancy requirements, typically two to four independent channels per range .

Beyond neutron flux, plants deploy area gamma monitors throughout containment, auxiliary buildings, fuel handling areas, and spent fuel pools to enforce occupational dose limits under 10 CFR 20. On-line gamma spectroscopy of the primary coolant monitors fission-product signatures that indicate fuel-cladding breaches. Containment atmosphere monitors classified as Category 1 under Regulatory Guide 1.97, Revision 5, must survive combined temperature, pressure, radiation, and chemical-spray environments for the full duration of a design-basis accident . Stack and liquid effluent monitors verify compliance with 10 CFR 50 Appendix I dose objectives, while the Radiological Environmental Monitoring Program tracks off-site air, water, and vegetation samples under RG 4.1.

The Fukushima Daiichi accident of March 2011 provided a severe demonstration of the consequences when monitoring fails. The tsunami rendered 23 of 24 on-site radiation monitoring stations nonfunctional. The subsequent loss of all AC power and battery depletion eliminated reactor vessel pressure, temperature, and water-level indication, forcing operators to manage three simultaneous core-melt progressions with essentially no real-time process data . Spent fuel pool instrumentation was unavailable for nearly two weeks. The NRC’s post-Fukushima response, including Order EA-12-051 requiring backup-powered spent fuel pool level instrumentation, the FLEX diverse-coping strategy described in NEI 12-06, and the addition of Type F severe-accident management variables to RG 1.97 Rev. 5, underscored that reliable monitoring is not a compliance formality but the operational foundation of accident management.

## Limitations of Current Radiation Detector Technologies

The detector materials deployed across the nuclear industry each carry critical limitations that constrain their use in existing plants and threaten to preclude their adoption in advanced reactor environments. High-purity germanium (HPGe) remains the gold standard for gamma spectroscopy, achieving better than 0.2% full-width at half-maximum energy resolution at 662 keV. However, its narrow bandgap of 0.67 eV mandates cryogenic operation below 120 K. Liquid-nitrogen dewars are impractical for unattended or remote monitoring; mechanical coolers add substantial cost, complexity, and microphonic noise that degrades resolution at low energies. HPGe is therefore confined almost exclusively to laboratory and assay applications rather than continuous in-plant monitoring .

Silicon detectors dominate charged-particle detection and, in research settings, are used for fast-neutron spectrometry via proton-recoil interactions , but suffer irreversible displacement damage above approximately 1014–1015 n​eq cm​−2 fluence, with charge-collection efficiency falling toward 50%, a threshold easily surpassed in the lifetime of a power-reactor instrument . Silicon’s low atomic number (Z=14) also provides poor photoelectric stopping power for gamma-ray energies above a few hundred keV, making it poorly suited to the mixed neutron-gamma fields present throughout a reactor plant.

Scintillators constitute the most widely deployed class of gamma-detection instruments and are valued for their ability to produce measurable light from a wide range of ionizing radiations. Sodium iodide thallium-doped [NaI(Tl)] crystals, the workhorse material, achieve approximately 6–7% energy resolution at 662 keV but are highly hygroscopic, mechanically fragile, and must be coupled to photomultiplier tubes that are sensitive to magnetic fields, fragile under shock and vibration, and require high-voltage supplies of 800–1200 V . Advanced scintillators such as LaBr​3(Ce) achieve approximately 3% resolution but contain intrinsic radioactivity from ​138La that creates a flat background continuum complicating low-level measurements. Organic scintillators, including plastic scintillators and stilbene crystals, are well established for fast neutron detection through proton-recoil interactions, but their low effective atomic number renders them essentially transparent to gamma rays, requiring either active discrimination electronics or companion gamma-shielding that adds mass, cost, and complexity.

Cadmium zinc telluride (CZT) represents the most mature room-temperature semiconductor alternative, offering energy resolutions approaching 0.7% at 662 keV in pixelated geometries with full single-carrier-transport correction. However, CZT crystal growth requires extremely precise control of stoichiometry and vapor-phase conditions during directional solidification: high cadmium vapor pressure promotes vacancy defects, tellurium inclusions limit boule diameter, and critical shear stresses of only 0.3 MPa make the material mechanically fragile during processing . Production costs remain high, supply is constrained, and the situation deteriorated significantly in 2025 when the People’s Republic of China imposed export controls on germanium, gallium, and related critical materials including cadmium telluride compounds.

For thermal neutron detection, the ​3He tube has been the standard technology since the 1950s by virtue of its high neutron absorption cross-section (5330 barns at 0.025 eV), excellent gamma discrimination, and compatibility with conventional pulse-counting electronics. The supply of ​3He, produced exclusively as a decay product of tritium from the nuclear-weapons stockpile, was recognized as critically constrained following the post-September 11 deployment of approximately 1,300 radiation portal monitors for border-security applications. Annual demand reached roughly 70,000 L against a production rate of only approximately 8,000 L yr​−1, driving prices from approximately $100 L​−1 to over $2,000 L​−1 and prompting DOE to begin rationing allocation in 2009 . The episode exposed the fragility of depending on a single non-renewable detection medium and has accelerated development of alternative neutron detectors using ​10B-lined tubes and ​6LiF:ZnS scintillator screens.

Halide perovskites have emerged as a compelling alternative class of radiation-responsive materials. Their high effective atomic number, CsPbBr​3 has Zeff=65.9, compared to 50.2 for CZT, provides excellent photoelectric stopping power for gamma radiation . Single-crystal MAPbBr​3 and CsPbBr​3 devices, operating at room temperature, have demonstrated mobility-lifetime products of up to 8×10−3 cm​2 V​−1 and energy resolutions approaching 1.4% at 662 keV , approaching CZT performance without cryogenic cooling or Bridgman growth. A distinctive self-healing mechanism, in which the soft perovskite lattice allows radiation-displaced ions to migrate back toward equilibrium positions at room temperature, has been confirmed under proton irradiation to 1013 p cm​−2 and extended gamma exposures . The methylhydrazinium lead chloride (MHyPbCl​3) composition investigated in this work introduces a high-hydrogen-density 3D perovskite framework with a hydrogen density of 3.79×1022 cm​−3 comparable to organic scintillators, enabling direct fast-neutron conversion through proton recoil without requiring a separate moderator or conversion layer .

Significant challenges remain. Ion migration under applied electric fields and elevated humidity drives hysteresis in current-voltage characteristics and accelerates device failure at the biases required for thick-crystal direct-conversion operation. Long-term stability data at power-reactor fluence levels (1014–1015 n cm​−2) remain absent from the literature. Lead toxicity presents regulatory and environmental considerations for deployed instruments. These challenges motivate the stabilization strategies, fluorinated surface passivation, hexagonal boron nitride composites, and vacuum operation, investigated in the present work.

## The Economics of Nuclear Instrumentation

Cost overruns in nuclear construction have become the defining obstacle to expansion in liberalized electricity markets. The two AP1000 units completed at Plant Vogtle in Georgia cost approximately $35 billion against an original estimate of $14 billion . France’s Flamanville 3 EPR reached 23.7 billion, seven times its original budget, after seventeen years of construction. The UK’s Hinkley Point C has escalated to an estimated £35 billion in 2015 prices against an initial projection of approximately £18 billion . New nuclear levelized cost of electricity in the United States ranges from approximately $110 MWh​−1 (EIA) to $180 MWh​−1 (Lazard), compared to approximately $55 MWh​−1 for utility-scale solar and $40 MWh​−1 for onshore wind. The existing U.S. fleet operates far more competitively, NEI reports a 2023 average total generating cost of $31.76 MWh​−1, the lowest on record , but twelve commercial reactors have closed since 2013 due to competitive pressure, and emergency support programs including a $6 billion Civil Nuclear Credit allocation have been required to prevent further premature retirements .

Instrumentation and control systems, while representing an estimated 5–10% of total plant capital cost, exert a disproportionate influence on both construction timelines and long-term operating expenses. A typical large light-water reactor contains approximately 10,000 sensors, 5,000 km of I&C cabling, and hundreds of electronic cabinets. Nuclear-grade quality assurance requirements under 10 CFR 50 Appendix B impose a cost premium that pervades the entire supply chain: components manufactured to identical functional specifications have been documented at price ratios of 4:1 or greater between nuclear-qualified and commercial-grade procurement, driven by QA documentation requirements, environmental qualification testing, and the severe scarcity of nuclear-qualified suppliers . Dominion Energy’s comprehensive digital I&C modernization across four units at Surry and North Anna is budgeted at $5.45 billion as part of subsequent license renewal . The DOE Light Water Reactor Sustainability (LWRS) Program has explicitly cautioned that “wide-scale modernization of legacy I&C systems could prove to be cost-prohibitive unless implemented to enable significant business innovation.”

The cost of radiation-hardened digital electronics amplifies this problem at the component level. Purpose-built radiation-hardened FPGAs, the Microchip RTG4, AMD/Xilinx XQRKU060, and their equivalents, carry price tags of tens of thousands to hundreds of thousands of dollars per device, a premium of 10× to 100× over commercial equivalents that cost $10–500 . The radiation-hardened FPGA market, valued at $465.5 million in 2024, serves primarily space and defense applications where unit volumes are small and alternatives do not exist. These devices trail commercial FPGAs by two to three process generations: the Microchip RTG4 uses a 65 nm flash-based process while commercial devices operate at 3–5 nm, a gap representing multiple orders of magnitude in logic density, performance, and power efficiency . Long lead times of 6–18 months, ITAR export restrictions, and the absence of advanced intellectual property cores compound the challenge. For SMRs targeting a levelized cost of electricity of $60–90 MWh​−1, this cost structure is untenable: I&C requirements do not scale down proportionally with reactor output, making instrumentation a higher fraction of total cost in smaller plants. The DOE’s GEMINA program has set an aspirational target of reducing advanced reactor operations and maintenance cost from $23 MWh​−1 to $2 MWh​−1 through autonomous operations and advanced diagnostics, a goal that cannot be achieved without fundamentally cheaper and more capable sensing and processing hardware .

The alternative to purpose-built rad-hard electronics is software-defined radiation tolerance using commercial off-the-shelf FPGAs with designer-inserted mitigation. Triple modular redundancy (TMR) triplicates critical logic with majority voting to correct single-event upsets in real time; configuration memory scrubbing periodically corrects bit-flip errors in SRAM-based FPGAs before they propagate; and partial dynamic reconfiguration enables real-time repair of corrupted fabric regions. CERN’s two-year study of Kintex-7 FPGAs under mixed-field radiation found no permanent operational failures to 300 krad total ionizing dose with TMR and scrubbing . Montana State University’s RadSat program demonstrated COTS FPGA-based radiation tolerance at “a cost 100× lower than existing radiation-hardened computers.” A TMR-with-spares architecture for nuclear reactor protection system logic has been validated under cyclotron irradiation . These results suggest that COTS FPGAs with mature mitigation strategies can meet nuclear monitoring requirements at a fraction of the cost of purpose-built rad-hard devices, provided the mitigation architecture is co-designed with the application from the outset.

## Research Objectives and Dissertation Organization

The research presented in this dissertation is organized around four complementary research thrusts aligned with the materials-to-systems hierarchy described above.

The first thrust characterizes the radiation response of photovoltaic-architecture halide perovskite solar cells operating as current-mode radiation monitors. Cs​0.1FA​0.9PbI​3 devices are evaluated under X-ray, ​137Cs gamma, and ​60Co gamma irradiation to establish the current-mode detection mechanism, dose-rate scaling, and long-term degradation behavior.

The second thrust develops and demonstrates perovskite semiconductor radiation detectors for direct-conversion operation under applied bias. This encompasses X-ray detection with MAPbI​3-hBN composite and two-dimensional perovskite devices, gamma spectroscopy with bromide perovskite single crystals, and fast-neutron detection using the hydrogen-rich MHyPbCl​3 composition. Ion migration under applied electric fields is identified and addressed as the central performance-limiting mechanism across all detector systems.

The third thrust investigates thermal radiation sensing as an alternative, non-electronic monitoring pathway for nuclear environments. Analytical thermal models are developed and experimentally validated for an Optical Fiber-Based Gamma Thermometer (OFBGT), and a proposed Optical Fiber-Based Neutron Dosimeter (OFBND) is evaluated through simulation.

The fourth thrust implements and validates radiation-tolerant FPGA-based digital instrumentation for nuclear monitoring. Two complementary benchmarks, a Flip-Flop Shift Register (FFSR) exercising reconfiguration and readback paths, and a fixed-point thermal control loop stressing arithmetic, control, and state evolution, are tested under fast neutron irradiation to characterize configuration memory upsets, latch-up susceptibility, and total ionizing dose effects in SRAM-based FPGAs.

The remainder of this dissertation is organized as follows. Chapter 2 provides the perovskite-focused background necessary for the materials and device investigations, encompassing perovskite crystal structure, radiation interaction physics, ion migration mechanisms, and the current state of perovskite-based radiation detectors. Chapter 3 provides the digital electronics background, covering radiation effects on semiconductor devices, single-event effects in SRAM-based FPGAs, and the taxonomy of fault-tolerant design approaches including triple modular redundancy and configuration scrubbing. Chapter 4 presents the characterization of Cs​0.1FA​0.9PbI​3 perovskite solar cells as current-mode radiation monitors under extended gamma irradiation. Chapter 5 consolidates the direct-conversion perovskite detector investigations, covering X-ray detection with MAPbI​3-hBN and two-dimensional perovskite devices, gamma spectroscopy with FAPbBr​3 and CsPbBr​3 single crystals, and fast-neutron detection with MHyPbCl​3. Chapter 6 describes the thermal radiation sensing concepts, including the OFBGT simulation, experimental validation, and the proposed OFBND design. Chapter 7 presents the FFSR digital electronics verification structure and its experimental results under fast neutron irradiation at the Ohio State University Research Reactor. Chapter 8 extends the FPGA irradiation campaign with a fixed-point thermal control benchmark that couples closed-loop feedback control, emulated plant dynamics, and dual-modular redundancy. Chapter 9 synthesizes the principal findings across all four research thrusts and identifies directions for future work.